## Slide 1
ARX LINEAR MODEL SET-UP FOR FAULT DIAGNOSIS OF GAS TURBINE SENSORS
R. Bettocchi P. R. Spina
Dipartimento di Ingegneria - Università di Ferrara
Via Saragat, 1 - 44100 Ferrara
Italy

## Slide 2
INTRODUCTION
Desire to reduce operating costs and improve overall reliability of gas turbines
Possibility of diagnostic system set-up with lower and lower costs
Increasing interest in
gas turbine fault diagnosis

## Slide 3
INTRODUCTION cont.
Analytical Redundancy: utilizes models of the system to calculate estimates of the measured output system variables
Use of linear models to simplifie their set-up and implementation
Great importance of the model set-up phase (the threshold of uncertainty in fault detection depends on model accuracy)

## Slide 4
INTRODUCTION cont.
System Modeling: consists in obtaining the I/O linear models by directly linearizing the physical law equations
System Identification: uses statistical methods to calculate model parameters from time series data measured on the machine

## Slide 5
FAULT DIAGNOSIS OF GAS TURBINE SENSORS
Models of the system to calculate estimates of the measured output system variables
Calculation of residuals (differences between computed and measured values of the same variables)
Sensor fault detection and isolation by means of the residual analysis

## Slide 6
FAULT DIAGNOSIS ... cont.
res (X) = f (x, x, F)
x : sensor fault vector (difference between measured and computed values)
x : measurement noise vector
F : matrix of model approximation

## Slide 7
FAULT DIAGNOSIS ... cont.
Exact model (F = 0) and absence of measurement noise (x = 0):
res (X) = F x

## Slide 8
FAULT DIAGNOSIS ... cont.
Fault Matrix
The elements of F matrix and x fault vector are substituted for value 0 or 1 on the basis of whether they are zero or not
Each column of the F matrix is the binary fault signature of the corresponding sensor
F matrix is called Fault Matrix or Incidence Matrix

## Slide 9
FAULT DIAGNOSIS ... cont.
Zero-threshold (deterministic ) fault isolation:
all the incidence matrix columns must be different from each other
One model for each output measured variable:
incidence matrix with the maximum number of elements per columns (maximum number of different fault signatures)

## Slide 10
FAULT DIAGNOSIS ... cont.
(O1) pressure at the compressor inlet
(O2) pressure at the compressor outlet
(O3) pressure at the turbine outlet
(O4) temperature at the compressor outlet
(O5) temperature at the turbine outlet
(O6) electrical power
(O7) rotational speed
(I1) IGV angular position
(I2) fuel mass flow rate
(I3) ambient temperature
(I4) ambient pressure

## Slide 11
SYSTEM MODELING
Linear models obtained starting from differential and algebraic non-linear equations of physical model, linearizing and transforming them in the z-domain
Actual case (27 equations):
  - linearization around the same operating point
  - transformation in the z-domain
  - reduction of the number of equations substituting the non-measured variables with the measured ones

## Slide 12
SYSTEM MODELING cont.

## Slide 13
Incidence Matrix
SYSTEM MODELING cont.
Residual
res (pic)
res (poc)
res (pot)
res (Toc)
res (Tot)
res (Pe)
pic
poc
pot
Toc
Tot
Pe

Mf
1
1
0
1
0
1
1
1
1
1
1
1
0
0
1
0
1
1
0
1
1
1
1
1
0
0
1
0
1
0
0
1
1
0
1
1
1
1
0
0
0
1
Ta
0
0
0
0
0
1
1
1
0
1
0
1
The first column of the matrix is equal to the last:
the zero-threshold fault isolation is not possible

## Slide 14
SYSTEM MODELING cont.
Residual
res (pic)
res (poc)
res (pot)
res (Toc)
res (Tot)
res (Pe)
pic
poc
pot
Toc
Tot
Pe

Mf
1
1
0
1
0
1
1
1
1
1
1
1
0
0
1
0
1
1
0
1
1
1
1
1
0
0
1
0
1
0
0
1
1
0
1
1
1
1
0
0
0
1
Ta
0
0
0
0
0
1
1
1
0
1
0
1
Desensitization of the six models in respect to ambient temperature (Ta)

## Slide 15
SYSTEM MODELING cont.
System modeling limits:
requires the analytical linearization of physical law equations
complicates some operations necessary to generate an incidence matrix allowing the fault isolation

## Slide 16
SYSTEM IDENTIFICATION
The system identification simplifies the linearization process:
  - parameter calculation performed starting from time series of transient operating condition data, by means of statistical methods of system identification

## Slide 17
SYSTEM IDENTIFICATION cont.
Orders [na (number of parameters at denominator), nb (number of parameters at numerator) and nk (delay)] determined from the transformation in the z-domain of the differential equations
ARX linear models

## Slide 18
SYSTEM IDENTIFICATION cont.
pic true and computed curves
poc true and computed curves

## Slide 19
SYSTEM IDENTIFICATION cont.
Maximum absolute values of residuals due to
model approximation obtained by adjusting the model orders
(ambient temperatures: 10-40 °C, load conditions: 70-100 %)
res(pic)
res(poc)
res(pot)
res(Toc)
res(Tot)
res(Pe)
9.0 x 10-6
2.0 x 10-5
1.2 x 10-6
6.0 x 10-5
2.0 x 10-4
1.5 x 10-4

## Slide 20
HIGH TRESHOLD FAULT ISOLATION
Non-zero response residuals due to model approximation and absence of measurement noise
(x = 0):
res (X) = F x + F x
The elements of residual vector are different from zero, even without sensor faults (x = 0), due to the model response errors (F 0)

## Slide 21
HIGH TRESHOLD... cont.
Threshold must be fixed for each residual, according to the size of maximum response error
Signature degradation phenomenon in the case of small faults (the presence of thresholds may determine that one or more residuals remain under the threshold)

## Slide 22
HIGH TRESHOLD... cont.
Toc residual due to a step fault of -2.5% of reference value on pic that occurs during a transient

## Slide 23
HIGH TRESHOLD... cont.
pic residual due to a step fault of -3% of reference value on poc that occurs during a transient

## Slide 24
HIGH TRESHOLD... cont.
Residual
res (pic)
res (poc)
res (pot)
res (Toc)
res (Tot)
res (Pe)
pic
poc
pot
Toc
Tot
Pe

Mf
1
1
0
0
0
1
0
1
1
1
1
1
0
0
1
0
1
1
0
1
1
1
1
1
0
0
1
0
1
0
0
1
1
0
1
1
1
1
0
0
0
1
0
0
0
0
0
1

## Slide 25
HIGH TRESHOLD... cont.
Desensitization of the models to make the high threshold fault isolation possible

## Slide 26
FAULT DETECTION ... cont.
Fault matrix
Failed sensor
Residual
res (pic)
res (poc)
res (pot)
res (Toc)
res (Tot)
res (Pe)
pic
poc
pot
Toc
Tot
Pe

Mf
1
1
1
0
0
1
1
1
1
1
0
1
0
1
1
1
1
1
1
1
1
1
1
1
0
0
1
0
1
1
0
1
0
1
1
1
0
0
1
0
1
0
0
0
0
0
0
1
1
1
0
0
0
1
0
1
1
0
1
1





## Slide 27
CONCLUSIONS
System identification is more suitable than system modeling for the model set-up in gas turbine sensor fault diagnosis
With system modeling it is much more difficult to calculate values of parameters and carry out operations which are necessary for making fault isolation possible
System identification makes all parameter calculation and desensitization operations of the models quite simple
System identification is suitable for utilization in the cases in which system physical laws are unknown

## Slide 28
Residual generation
I/0 linear model in the z-domain:
y : output vector
u : input vector
v : process fault vector
w : process noise vector

## Slide 29
Parity equations :
e (z) : residual vector
: input-output combined vector
: matrix of transfer function of estimated
system
: matrix of transfer function of
physical system
x : sensor fault vector (difference between
measured and computed values)
x : measurement noise vector
F : matrix of model approximation

## Slide 30
Sensor fault only (v , w = 0):
Exact model (F = 0) and absence of measurement noise (x = 0):